## VV22
0.6/1kV-1 core copper conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
1X10 | 1 | 0.2 | 1.8 | 12.39 | 290.1427 | 1.83 | 50 | 70
1X16 | 1 | 0.2 | 1.8 | 13.5 | 370.8826 | 1.15 | 66 | 92
1X25 | 1.2 | 0.2 | 1.8 | 15.16 | 488.8928 | 0.727 | 85 | 115
1X35 | 1.2 | 0.2 | 1.8 | 15.8 | 594.5513 | 0.524 | 105 | 140
1X50 | 1.4 | 0.2 | 1.8 | 17.5 | 752.6402 | 0.387 | 125 | 175
1X70 | 1.4 | 0.2 | 1.8 | 19.1 | 973.5037 | 0.268 | 160 | 205
1X95 | 1.6 | 0.2 | 1.8 | 21.1 | 1260.2308 | 0.193 | 195 | 250
1X120 | 1.6 | 0.2 | 1.8 | 22.5 | 1521.8688 | 0.153 | 235 | 290
1X150 | 1.8 | 0.2 | 1.8 | 24.5 | 1857.8851 | 0.124 | 265 | 325
1X185 | 2 | 0.2 | 1.7735 | 26.447 | 2229.7745 | 0.0991 | 300 | 365
1X240 | 2.2 | 0.2 | 1.8645 | 29.229 | 2834.644 | 0.0754 | 355 | 420
1X300 | 2.4 | 0.2 | 1.9485 | 31.997 | 3480.8828 | 0.0601 | 410 | 475
1X400 | 2.6 | 0.5 | 2.127 | 37.254 | 4848.1176 | 0.047 | 480 | 540
1X500 | 2.8 | 0.5 | 2.232 | 41.464 | 6055.5379 | 0.0366 | 550 | 610
1X630 | 2.8 | 0.5 | 2.3405 | 45.081 | 7406.4762 | 0.0283 | 645 | 735
0.6/1kV-2 core copper conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
2X2.5 | 0.8 | 0.2 | 1.8 | 13.5 | 249.2 | 7.41 | - | -
2X4 | 1 | 0.2 | 1.8 | 15.3 | 361.5 | 4.61 | - | -
2X6 | 1 | 0.2 | 1.8 | 16.3 | 427 | 3.08 | - | -
2X10 | 1 | 0.2 | 1.8 | 18.98 | 572.4083 | 1.83 | 50 | -
2X16 | 1 | 0.2 | 1.8 | 21.2 | 748.8869 | 1.15 | 66 | -
2X25 | 1.2 | 0.2 | 1.8 | 24.52 | 1011.6526 | 0.727 | 85 | -
2X35 | 1.2 | 0.2 | 1.8 | 25.8 | 1235.0895 | 0.524 | 105 | 105
2X50 | 1.4 | 0.2 | 1.854 | 29.308 | 1593.5479 | 0.387 | 125 | 125
2X70 | 1.4 | 0.2 | 1.952 | 32.704 | 2089.1196 | 0.268 | 160 | 155
2X95 | 1.6 | 0.5 | 2.148 | 38.896 | 3170.196 | 0.193 | 195 | 185
2X120 | 1.6 | 0.5 | 2.2481 | 41.8962 | 3792.8596 | 0.153 | 235 | 215
2X150 | 1.8 | 0.5 | 2.372 | 45.944 | 4601.8402 | 0.124 | 265 | 235
2X185 | 2 | 0.5 | 2.519 | 50.638 | 5568.7385 | 0.0991 | 300 | 265
0.6/1kV-3 core copper conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X2.5 | 0.8 | 0.2 | 1.8 | 14.3 | 323 | 7.41 | - | -
3X4 | 1 | 0.2 | 1.8 | 16.1372 | 422.1269 | 4.61 | - | -
3X6 | 1 | 0.2 | 1.8 | 17.2578 | 509.4747 | 3.08 | - | -
3X10 | 1 | 0.2 | 1.8 | 19.9084 | 698.0462 | 1.83 | 50 | 70
3X16 | 1 | 0.2 | 1.8 | 22.3005 | 934.692 | 1.15 | 66 | 92
3X25 | 1.2 | 0.2 | 1.8 | 25.8778 | 1283.8909 | 0.727 | 85 | 115
3X35 | 1.2 | 0.2 | 1.786 | 27.2289 | 1599.243 | 0.524 | 105 | 140
3X50 | 1.4 | 0.2 | 1.9145 | 31.1495 | 2093.1057 | 0.387 | 125 | 175
3X70 | 1.4 | 0.2 | 2.0343 | 35.2371 | 2816.8501 | 0.268 | 160 | 205
3X95 | 1.6 | 0.5 | 2.2275 | 41.349 | 4141.1265 | 0.193 | 195 | 250
3X120 | 1.6 | 0.5 | 2.3356 | 44.5823 | 5003.1394 | 0.153 | 235 | 290
3X150 | 1.8 | 0.5 | 2.4834 | 49.3724 | 6166.998 | 0.124 | 265 | 325
3X185 | 2 | 0.5 | 2.6271 | 53.9697 | 7426.3475 | 0.0991 | 300 | 365
3X240 | 2.2 | 0.5 | 2.8376 | 60.6093 | 9480.3136 | 0.0754 | 355 | 420
3X300 | 2.4 | 0.5 | 3.0191 | 66.3597 | 11584.4176 | 0.0601 | 410 | 475
0.6/1kV-4 core copper conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X2.5 | 0.8 | 0.2 | 1.8 | 14.9 | 382 | 7.41 | - | -
4X4 | 1 | 0.2 | 1.8 | 17.2354 | 496.6414 | 4.61 | - | -
4X6 | 1 | 0.2 | 1.8 | 18.4906 | 607.4702 | 3.08 | - | -
4X10 | 1 | 0.2 | 1.8 | 21.4599 | 847.6422 | 1.83 | 50 | 70
4X16 | 1 | 0.2 | 1.8 | 24.1394 | 1147.9199 | 1.15 | 66 | 92
4X25 | 1.2 | 0.2 | 1.7756 | 28.0978 | 1590.4478 | 0.727 | 85 | 115
4X35 | 1.2 | 0.2 | 1.8688 | 29.8291 | 2017.7465 | 0.524 | 105 | 140
4X50 | 1.4 | 0.2 | 2.0268 | 34.6489 | 2689.5582 | 0.387 | 125 | 175
4X70 | 1.4 | 0.5 | 2.1873 | 40.0325 | 3980.0852 | 0.268 | 160 | 205
4X95 | 1.6 | 0.5 | 2.3567 | 45.4407 | 5230.284 | 0.193 | 195 | 250
4X120 | 1.6 | 0.5 | 2.4919 | 49.4905 | 6403.1741 | 0.153 | 235 | 290
4X150 | 1.8 | 0.5 | 2.6418 | 54.377 | 7848.3887 | 0.124 | 265 | 325
4X185 | 2 | 0.5 | 2.8167 | 59.9548 | 9544.5663 | 0.0991 | 300 | 365
4X240 | 2.2 | 0.5 | 3.0369 | 66.9131 | 12140.133 | 0.0754 | 355 | 420
4X300 | 2.4 | 0.5 | 3.2402 | 73.3546 | 14881.2925 | 0.0601 | 410 | 475
0.6/1kV-5 core copper conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
5X2.5 | 0.8 | 0.2 | 1.8 | 16.126 | 434.6587 | 7.41 | - | -
5X4 | 1 | 0.2 | 1.8 | 18.448 | 584.7338 | 4.61 | - | -
5X6 | 1 | 0.2 | 1.8 | 19.852 | 713.2203 | 3.08 | - | -
5X10 | 1 | 0.2 | 1.8 | 23.173 | 1012.8532 | 1.83 | 50 | 70
5X16 | 1 | 0.2 | 1.8 | 26.17 | 1371.6581 | 1.15 | 66 | 92
5X25 | 1.2 | 0.2 | 1.854 | 30.76 | 1925.6905 | 0.727 | 85 | 115
5X35 | 1.2 | 0.2 | 1.958 | 32.6959 | 2456.033 | 0.524 | 105 | 140
5X50 | 1.4 | 0.5 | 2.1746 | 39.3192 | 3664.2936 | 0.387 | 125 | 175
5X70 | 1.4 | 0.5 | 2.3069 | 43.9038 | 4826.2848 | 0.268 | 160 | 205
5X95 | 1.6 | 0.5 | 2.5099 | 50.3798 | 6422.8434 | 0.193 | 195 | 250
5X120 | 1.6 | 0.5 | 2.6422 | 54.4244 | 7812.769 | 0.153 | 235 | 290
5X150 | 1.8 | 0.5 | 2.8263 | 60.3226 | 9664.7005 | 0.124 | 265 | 325
5X185 | 2 | 0.5 | 3.0059 | 66.0817 | 11692.1673 | 0.0991 | 300 | 365
5X240 | 2.2 | 0.5 | 3.2515 | 73.8631 | 14909.268 | 0.0754 | 355 | 420
5X300 | 2.4 | 0.5 | 3.4924 | 81.4947 | 18394.165 | 0.0601 | 410 | 475
0.6/1kV-3+1 core copper conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3*4+1*2.5 | 1.0/0.8 | 0.2 | 1.8 | 16.7405 | 666.8205 | 4.61/7.41 | - | -
3*6+1*4 | 1.0/1.0 | 0.2 | 1.8 | 18.2046 | 580.9888 | 3.08/4.61 | - | -
3*10+1*6 | 1.0/1.0 | 0.2 | 1.8 | 20.7517 | 786.6938 | 1.83/3.08 | 50 | 70
3*16+1*10 | 1.0/1.0 | 0.2 | 1.8 | 23.5104 | 1073.6552 | 1.15/1.83 | 66 | 92
3*25+1*16 | 1.2/1.0 | 0.2 | 1.8 | 27.1949 | 1496.7697 | 0.727/1.15 | 85 | 115
3*35+1*16 | 1.2/1.0 | 0.2 | 1.8137 | 28.3839 | 1795.1195 | 0.524/1.15 | 105 | 140
3*50+1*25 | 1.4/1.2 | 0.2 | 1.9535 | 32.8379 | 2395.5517 | 0.387/0.727 | 125 | 175
3*70+1*35 | 1.4/1.2 | 0.5 | 2.1217 | 37.9809 | 3584.28 | 0.268/0.524 | 160 | 205
3*95+1*50 | 1.6/1.4 | 0.5 | 2.2847 | 42.9655 | 4669.1953 | 0.193/0.387 | 195 | 250
3*120+1*70 | 1.6/1.4 | 0.5 | 2.4192 | 47.325 | 5825.0422 | 0.153/0.268 | 235 | 290
3*150+1*70 | 1.8/1.4 | 0.5 | 2.5317 | 50.9983 | 6804.1777 | 0.124/0.268 | 265 | 325
3*185+1*95 | 2.0/1.6 | 0.5 | 2.6947 | 56.1644 | 8430.4464 | 0.0991/0.193 | 300 | 365
3*240+1*120 | 2.2/1.6 | 0.5 | 2.9042 | 62.7308 | 10700.9427 | 0.0754/0.153 | 355 | 420
3*300+1*150 | 2.4/1.8 | 0.5 | 3.0941 | 68.8582 | 13115.1274 | 0.0601/0.124 | 410 | 475
0.6/1kV-4+1 core copper conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4*4+1*2.5 | 1.0/0.8 | 0.2 | 1.8 | 17.9836 | 545.0635 | 4.61/7.41 | - | -
4*6+1*4 | 1.0/1.0 | 0.2 | 1.8 | 19.5712 | 682.9915 | 3.08/4.61 | - | -
4*10+1*6 | 1.0/1.0 | 0.2 | 1.8 | 22.5088 | 940.5438 | 1.83/3.08 | 50 | 70
4*16+1*10 | 1.0/1.0 | 0.2 | 1.8 | 25.5706 | 1295.2383 | 1.15/1.83 | 66 | 92
4*25+1*16 | 1.2/1.0 | 0.2 | 1.8256 | 29.8069 | 1826.7695 | 0.727/1.15 | 85 | 115
4*35+1*16 | 1.2/1.0 | 0.2 | 1.9088 | 31.3556 | 2230.9321 | 0.524/1.15 | 105 | 140
4*50+1*25 | 1.4/1.2 | 0.5 | 2.1217 | 37.9498 | 3382.9315 | 0.387/0.727 | 125 | 175
4*70+1*35 | 1.4/1.2 | 0.5 | 2.2483 | 42.0046 | 4431.8778 | 0.268/0.524 | 160 | 205
4*95+1*50 | 1.6/1.4 | 0.5 | 2.4456 | 48.2533 | 5918.6546 | 0.193/0.387 | 195 | 250
4*120+1*70 | 1.6/1.4 | 0.5 | 2.5802 | 52.4104 | 7232.4429 | 0.153/0.268 | 235 | 290
4*150+1*70 | 1.8/1.4 | 0.5 | 2.714 | 56.782 | 8524.2778 | 0.124/0.268 | 265 | 325
4*185+1*95 | 2.0/1.6 | 0.5 | 2.9095 | 63.0269 | 10632.7819 | 0.0991/0.193 | 300 | 365
4*240+1*120 | 2.2/1.6 | 0.5 | 3.133 | 70.0621 | 13463.2588 | 0.0754/0.153 | 355 | 420
4*300+1*150 | 2.4/1.8 | 0.5 | 3.3619 | 77.3459 | 16582.342 | 0.0601/0.124 | 410 | 475
0.6/1kV-3+2 core copper conductor PVC insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3*4+2*2.5 | 1.0/0.8 | 0.2 | 1.8 | 17.5192 | 516.508 | 4.61/7.41 | - | -
3*6+2*4 | 1.0/1.0 | 0.2 | 1.8 | 19.2904 | 657.4291 | 3.08/4.61 | - | -
3*10+2*6 | 1.0/1.0 | 0.2 | 1.8 | 21.8446 | 884.1957 | 1.83/3.08 | 50 | 70
3*16+2*10 | 1.0/1.0 | 0.2 | 1.8 | 24.9712 | 1223.0893 | 1.15/1.83 | 66 | 92
3*25+2*16 | 1.2/1.0 | 0.2 | 1.8803 | 28.9118 | 1718.4737 | 0.727/1.15 | 85 | 115
3*35+2*16 | 1.2/1.0 | 0.2 | 1.9166 | 30.0212 | 2016.8727 | 0.524/1.15 | 105 | 140
3*50+2*25 | 1.4/1.2 | 0.2 | 2.0988 | 35.5916 | 2773.8777 | 0.387/0.727 | 125 | 175
3*70+2*35 | 1.4/1.2 | 0.5 | 2.2504 | 40.2268 | 4039.6356 | 0.268/0.524 | 160 | 205
3*95+2*50 | 1.6/1.4 | 0.5 | 2.4337 | 45.8315 | 5328.815 | 0.193/0.387 | 195 | 250
3*120+2*70 | 1.6/1.4 | 0.5 | 2.5876 | 50.5352 | 6666.1775 | 0.153/0.268 | 235 | 290
3*150+2*70 | 1.8/1.4 | 0.5 | 2.6953 | 53.8287 | 7629.058 | 0.124/0.268 | 265 | 325
3*185+2*95 | 2.0/1.6 | 0.5 | 2.9021 | 60.1502 | 9630.498 | 0.0991/0.193 | 300 | 365
3*240+2*120 | 2.2/1.6 | 0.5 | 3.1081 | 66.4482 | 12088.0989 | 0.0754/0.153 | 355 | 420
3*300+2*150 | 2.4/1.8 | 0.5 | 3.3217 | 72.9774 | 14753.7115 | 0.0601/0.124 | 410 | 475